## Summary
Key Parameters | Results
Combined Data Set SCC List | 50100802
Does the SCC contain more than 15 sources? | Yes
Pollutant | 2,3,7,8-TETRACHLORODIBENZOFURAN
Units | LB
Activity | TONS DRIED SLUDGE FED
Factor Quality Rating | Moderately Representative
Number of individual test data values used to calculate the emissions factor | 8
Number of individual test data values excluded from the calculation | 2
Composite Test Rating | 75.3
Control Device Configuration | AFTERBURNER,VENTURI SCRUBBER
AFTERBURNER,WET SCRUBBER
ELECTROSTATIC PRECIPITATOR - WET (WESP),IMPINGEMENT PLATE SCRUBBEREGENERATIVE THERMAL OXIDIZER,VENTURI SCRUBBER;
ELECTROSTATIC PRECIPITATOR - WET (WESP),PACKED BED SCRUBBER - HIGH EFFICIENCY,QUENCH TOWEREGENERATIVE THERMAL OXIDIZER;
VENTURI SCRUBBER
New Candidate Factor Value | 7.02e-11

## Data Included
Individual Test Data Value | Individual Test Method | Individual Test Data Units | Individual Test Data Activity | Individual Test Rating | Detection Limit Flag | Year of Test | Facility Name | Control_1 | Control_2 | Control_3 | Control_4 | Test City | Test State | ERT Project Data Set | Submission_ID
7.62e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 64 | ADL | 2015 | City of Palo Alto Water Quality Control Plant | AFTERBURNER | WET SCRUBBER |  |  | Palo Alto | CA | PDS | 80121521
4.09e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 75 | ADL | 2016 | Erie Waste Water Treatment Plant | VENTURI SCRUBBER |  |  |  | Erie | PA | PDS | 80135251
2.88e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 75 | BDL | 2017 | Blue River Wastewater Treatment Plant | AFTERBURNER | VENTURI SCRUBBER | VENTURI SCRUBBER |  | Kansas City | MO | PDS | 80272499
9.76e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 78.5 | ADL | 2020 | Hatfield Township Municipal Authority | IMPINGEMENT PLATE SCRUBBER | REGENERATIVE THERMAL OXIDIZER | VENTURI SCRUBBER | ELECTROSTATIC PRECIPITATOR - WET (WESP) | Colmar | PA | PDS | 80680327
2e-10 | Method 23 | LB | TONS DRIED SLUDGE FED | 78.5 | ADL | 2017 | Atlantic County Utilities Authority | AFTERBURNER | WET SCRUBBER |  |  | Atlantic City | NJ | PDS | 80756246
4.75e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 78.5 | ADL | 2017 | Atlantic County Utilities Authority | WET SCRUBBER | AFTERBURNER |  |  | Atlantic City | NJ | PDS | 80756572
2.14e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 78.5 | ADL | 2020 | Atlantic County Utilities Authority | WET SCRUBBER | AFTERBURNER |  |  | Atlantic City | NJ | PDS | 81081160
4.95e-11 | Method 23 | LB | TONS DRIED SLUDGE FED | 78.5 | ADL | 2019 | DELCORA | PACKED BED SCRUBBER - HIGH EFFICIENCY | ELECTROSTATIC PRECIPITATOR - WET (WESP) | QUENCH TOWER | REGENERATIVE THERMAL OXIDIZER | Chester | PA | PDS | 81141860

## Data Excluded
Reason for Exclusion | Individual Test Data Value | Individual Test Method | Individual Test Data Units | Individual Test Data Activity | Individual Test Rating | Detection Limit Flag | Year of Test | Facility Name | Control_1 | Control_2 | Control_3 | Test City | Test State | ERT Project Data Set | Submission_ID
Data value does not improve the factor quality rating. | 8.55e-12 | Method 23 | LB | TONS DRIED SLUDGE FED | 25 | BDL | 2016 | Blue River Wastewater Treatment Plant | AFTERBURNER | VENTURI SCRUBBER |  | Kansas City | MO | PDS | 80162371
Data value does not improve the factor quality rating. | 6.62e-11 | Method 24 | LB | TONS DRIED SLUDGE FED | 32 | DLL | 2016 | City of Palo Alto Water Quality Control Plant | AFTERBURNER | WET SCRUBBER |  | Palo Alto | CA | PDS | 80180329